WESTCO PUMP DATA SHEET		1매 1매중
PAGE
Client		Item No
Job No		Location
1	NOTE : ○ Indicate Information to be completed by Purchaser □ By Manufacturer
2	Service :
3	No. Pumps Req`d		No. Motor Req`d		Item No.		Provided By	EU YEON	Mtd By	EU YEON
4			No. Motor Req`d		Item No.		Provided By		Mtd By
5	Pump Mfr	EU YEON	Size & Type	SS - 1575	Mfg. No.
6	OPERATING CONDITION EACH PUMP	PERFORMANCE
7	Liquid	water	㎥/min at nor./rated	/ 0.012	Proposal Curve No.
8			Disch. Press. Kg/㎠g		No. of Stages	1	RPM	3,450
9	PT ℃	AMB	MAX		Suc. Press Kg/㎠g Max		Rated	Suction	● Single	○ Double
10	Spec. Gravity at PT.	1.000	Diff. Press. Kg/㎠g	10.0	NPSH Req`d (water)	0.4	m
11	Vap. Press. at PT㎏/㎠A		Diff. Head m	100.0	Des. Eff.	29	%	0.674	kw rated
12	Visc. at PT		NPSH Avail. m at Pump	0.4	Max. kw Rated lpm		kw rated
13	Corr / Eros Casued By		Hydraulic Power, KW		KW	Max. Head Rated lpm		m
14	CONSTRUCTION	Min. Continuous		㎥/min
15	NOZZLES	SIZE	RATING	FACING	LOCATION	Rotating Facing Coupling	● CW	○ CCW
16	Suction	20 A	-	PT	SIDE	SHOP TEST
17	Discharge	20 A	-	PT	SIDE	Non. Wit Perf	●	Wit. Perf	○
18	Case - Mount	□ Centerline	■ Foot	□ Bracket	□ Vertical	Non. Wit Hydro	●	Wit. Hydro	○
19	- Split	□ Axial	■ Radial	Non NPSH	●	Wit. NPSH	○
20	- Type	■ Single Volute	□ Double Volute	□ Diffuser	Shop Inspection	●
21	- Press	Max. Allow	12	㎏/㎠		℃	Hydro test	16	㎏/㎠	Dismant & lnp. After Test	○
22	- Connect	□ Vent	■ Drain	□ Gauge	Other		○
23	Impeller Dia Rated	85	mm MAX	85	mm TYPE	CLOSED
24	Mount	□ Between Brgs.	■ Over hung	MATERIAL
25	Bearing Type	□ Radial	N / A	□ Thrust	N / A	Pump Casing	●	SSC 13
26	Lub	□ Self	■ Flood	□ Ring Oil	□ Grease	Impeller	●	STS 304
27		□ Pressure		Kg/㎠g	□ Constant Level Oiler	Shaft	●	STS 304
28	Coupling & Guard	□ Mfr.	□ Model	Wear Rings	○
29	Driver half Mtd By	□ Pump Mfr	□ Driver Mfr	□ Purchaser	Base Plate	○
30	Packing	□ Mfr & Type	□ Size / No. of Rings	VERTICAL PUMP
31	Mech. Seal	■ Mfr & Type	JUKJEON - 14∅	□ API Class Code	Pit or Sump Depth	○	mm
32		□ Mfr Code		Min. Submer ge Req`d	□	mm
33	AUXILIARY PIPING	Column Pipe	□ Flanged	□ Thread
34	□ C.W. Pipe Plan		○ Material		Line Shaft	□ Open	□ Closed
35	□ Total C.W. Req`d		○ Sight F.I. Req`d		Brgs	□ Bowl	□ Line Shaft
36	□ Packing Cool Inj Req`d	□ Total	㎥ / hr □	Kg/㎠g	Brgs Lube	□ Water	□ Oil	□ Grease
37	□ Seal Flush Pipe Plan		□ Material		Float & Rod Mat.	○
38	□ Ext. Seal Flush Fluid	㎥ / hr		Kg/㎠g	Float Switch	□
39	□ Aux. Seal Plan		□ Material		Pump Thrust	□ UP	□ DOWN
40	□ Aux. Seal Quench Fluid				WEIGHT
41	MOTOR DRIVER	Pump	20	㎏	Base		㎏
42	KW	0.75	RPM	3,450	Frame	80	Motor		㎏	Engine		㎏
43	Voltage	220/380	Phase	3	Cycle	60	APPLICABLE SECTIONS
44	Mfr.	SAMIL	Type	EYM-0750	Pole	2	○ Pumps
45	Lube	Grease			Full Load Amp`s		○ Motor
46	Insul	F	Enbe	TEFC	Temp Rise	40℃	○ Painting
47	Bearing	Front	6204ZZ		Rear	6202ZZ	○ Noise
48	ENGINE DRIVER	REMARKS
49	HP		rpm
50	Mfr,		Type
51	REMARKS
52
53
54
	ISSUE	DATE
EU YEON WESTEC CO., LTD	REV. 2	2008.07.08
SSL301-2-R3)		210X297